## Slide 1: Midlende nivåregulering av buffertank (eng.: averaging level control...)
Av Finn Aakre Haugen
(finn.haugen@usn.no)
IA3112 Automatiseringsteknikk Høsten 2017

## Slide 2
2
Buffer tank with a level control system
Aim: Averageing (or equalizing, or attenuating) inflow variations so that the outflow becomes smoother than the inflow.

## Slide 3
3
Example of application (results shown at end of this PPT): Level control of equalization magazine upstreams the
VEAS water resource recovery facility (wrrf) or resource recovery facility (wrrf), at Slemmestad, south of Oslo, Norway:

## Slide 4
4
How to tune LC?
We need a sluggish or soft or compliant LC so that the liquid volume (the level) can take up the inflow variations.
Ziegler-Nichols is useless here since it gives fast or stiff control :-(
But Skogestad is excellent, using Tc as tuning parameter :-)
Kc = 1/(Ki*Tc) Ti = 2*Tc
where Ki = -1/A is the integrator gain or normalized process step response.
How to select Tc?

## Slide 5
5
...
How to select Tc?
As a start, assume P (proportional) level controller. It can be shown, from a mathematical model of the level control system, that
Δhmax = (Tc/A)*ΔFin
where Δhmax is corresponding maximum allowed level change (in steady state) after max inflow step change, ΔFin.
With a PI controller with the same Tc:
Δhmax <= (Tc/A)*ΔFin
Solving this inequality for Tc gives
Tc >= A* Δhmax/ΔFin
=> Specification of Tc in the PI settings:
Tc = A* Δhmax/ΔFin

## Slide 6
6
Comparison of responses in level h
due to step change in inflow Fin, with P and with PI controllers:

## Slide 7
7
Example
Assumptions:
A = 2000 m2
ΔFin = 1 m3/s
Δhmax = 0.5 m
Resulting Tc:
Tc = A* Δhmax/ΔFin = 2000*(-0.5)/(-1) = 1000 s
PI settings:
Kc = 1/(Ki*Tc) = -A/Tc = -2000 m2 / 1000 s = 2.0 (m3/s)/m
Ti = 2*Tc = 2*1000 s = 2000 s

## Slide 8
8
Simulation!

## Slide 9
9
Results from VEAS:
With original PI settings in the LC
(Kc = 8.0 , Ti = 1000 s)
With new (Skogestad) PI settings in the LC (Kc = 3.1 , Ti = 3240 s)
Much smoother pump flow
Pump flow