## Slide 1: Gain scheduling
Av Finn Aakre Haugen
(finn.haugen@usn.no)
IA3112 Automatiseringsteknikk og EK3114 Automatisering og vannkraftregulering
Høstsemesteret 2017

## Slide 2
Solutions:
Conservative tuning (good stability, but sluggish control)
Adaptive tuning (optimal settings all the time, i.e. the control system gets good stability and fast control):
  Model-based PID parameter adjustment
  Gain scheduling based on experiments
Problem: Assume that the dynamic properties of the process to be controlled vary with the operating point. With fixed PID settings, the control system may
get poor stability, or
become sluggish
Here, we concentrate on Gain scheduling.
2

## Slide 3
Control system with controller parameter
updating using Gain scheduling:
3

## Slide 4
Gain schedule
= Table of sets (here 3) of PID parameter values:
4
PID set 1
PID set 2
PID set 3

## Slide 5
5
PID set 1
PID set 2
PID set 3
How to interpolate between the tabular values of
controller parameters and GS variable?
Let's focus on controller gain Kp (the same principles apply to Ti and Td as well).

## Slide 6
How to interpolate between the tabular values of
controller parameters and GS variable?
6

## Slide 7
An example: Temperature control system
where process dynamics varies with flow
7

## Slide 8
Process gain
~
Inverse of flow
Time constant
~
Inverse of flow
Time delay
~
Inverse of flow
In the example:
How do process parameters depend on flow?
Responses in temperature after 10% step in control signal to heater:
Large flow (24 kg/min)
Small flow (12 kg/min)
8

## Slide 9
Process gain
~
Inverse of flow
Time constant
~
Inverse of flow
Time delay
~
Inverse of flow
Implication: When PID controller has fixed parameters:
If flow is reduced, the stability of
the control loop is reduced.
By adjusting the controller parameters based on flow measurement!
So, flow is selected as GS variable.
How to maintain stability and speed of the control system despite flow variations?
Observations (from previous slide):

## Slide 10
  Simulator:
Gain scheduling
10