## Slide 1: How a control system may become unstable
By Finn Aakre Haugen
(finn.haugen@hit.no)
Course PEF3006 Process Control Fall 2017

## Slide 2: Control loop:
Typical causes of reduced stability or even instability of a control loop:
Increase of loop gain
Increase of loop dead-time
Increase of loop time-constants
2

## Slide 3
  Let’s impose various parameter changes on this simulator:
Level control of wood-chip tank
  Increase of loop gain:
    Controller:
      Controller gain (observe the effect of increase)
      Integral time (decrease)
    Actuator: Feed screw gain (increase)
    Process: Cross sectional area (decrease)
    Sensor: Sensor gain (increase)
  Increase of time-delay:
    Process: Transportation time (increase)
  Increase of time-constant:
    Measurement filter: Time-constant in filter (increase)
3
  And we will use Skogestad's PI tuning formula to readjust
  the PI settings to cope with stability problems!
  Recall the PI formulas: Kp = 1/(2*Ki*tau), Ti = 4*tau