## Slide 1: PID Control
Course: Process Control, NMBU
Dec 2017 - April 2018
By Finn Aakre Haugen, PhD, TechTeach
(finnhaugen@hotmail.com)

## Slide 2
Reviewing the feedback control loop:

## Slide 3
(PID = Proportional + Integral + Derivative)
e – control error = ysp - ym
u – total control signal
u0, or uman, – manual control signal
up – proportional term
ui – integral term
ud – derivative term
Kp – controller gain = 100/PB
Ti – integral time [sec or min]
Td – derivative time [sec or min]
The PID controller function
Variables (signals):
Parameters (constants):
Control error
e
Control signal
u
PID
P
I
D

## Slide 4: The PID controller function (cont.)
I-term, ui, and therefore total control signal, u, will change (increase or decrease) as long as control error is different from zero, causing the error to eventually become zero (in steady-state).
P- and D-term contributes with speed in control action. D-term can also provide increased stability (damping). Unfortunately, D-term amplifies measurement noise. Therefore, the D-term is quite unpopular, and is often not used.

## Slide 5
Discrete-time (computer-based) PID control loop:
(Hoping that the block diagram is understandable despite the Norwegian text.)

## Slide 6
e(k)
PID
P
I
D
u(k) = uman + up(k) + ui(k) + ud(k)
u(k) is calculated by the PID algorithm each time step, Ts. (A typical Ts in process controllers is 0.1 s.)
The P, I, and D terms can be calculated as shown on the next slide.
Discrete-time PID controller
Introducing simplifyes notation: e(k) = e(tk) og u(k) = u(tk)

## Slide 7
Discrete-time PID algorithm based on discrete-time version of the continuous-time PID function:
up(k) = Kp*e(k)
P:
ui(k) = (Kp/Ti)*Ts*[e(1)+…+e(k-1)+e(k)]
I:
ud(k) = Kp*Td*[e(k)-e(k-1)]/Ts
D:
D term is prop. to the rate of change of the control error:
P term is proportional with the current control error:
I term is prop. to the sum of all sampled errors, i.e. accumulated error:
= ui(k-1) + (Kp/Ti)*Ts*e(k)
The second row is an alternative, practical implementation of the I term since the additions of old errors are avoided.
Ideally, the D term increases control speed and stability. Howerver, the D term unfortunately is very sensitive to measurement noise, causing the control signal to become noisy. Therefore, often the d term is not used (Td = 0).
The I term ensures zero steady-state error because the I term - and therefore the total control signal (u) - is adjusted whenever the control error is different from zero. So, the controller will keep on improving.
The term alone can not give zero error (in steady state) since there must be a error different from zero in order for any compensation to take place. So, there will be some compensation, but not big enough to give zero error.

## Slide 8: Measurement filter
Purpose of the filter: To smooth noisy measurement signal, thereby causing the control signal to become smoother.
Which filter to use? A time-constant filter is commonly used.
How to select the time-constant: Trial-and-error. Typical value in industrial control loops: A few seconds (e.g. 2 or 5 sec).
With meas filter:
Without meas filter:

## Slide 9
  Let’s try:
Level control of wood-chip tank
(where we study the the P-, D-, and I-terms of the control signal - with and without measurement noise.)